## Slide 1
Wavewin Sniffer 24 Configuration & Polling Software
(Wavewin Sniffer Operations Guide)

## Slide 2
Operations Guide Content IRIG-B Timing

## Slide 3
IRIG-B Timing
Configuring a Channel for Data Timing
“CBL-IRIG-B”
Connect the IRIG-B Cable to the Unmodulated
IRIG-B Port on the GPS Clock

## Slide 4
Step 1: Enter “GPS IRIG-B” in the “Channel Titles” field.

## Slide 5
Step 2: In “Configuration” tab, select “CBL-IRIG-B”.

## Slide 6
Step 3: Save the active configuration to disk.

## Slide 7
Step 4: Click “Start Recorder” to begin polling.

## Slide 8
Step 5: When the “Locked” indicator turns green,
the Wavewin Sniffer 24 is synchronized. If the
indicator does not turn green, follow the next slides:

## Slide 9
Customized IRIG-B Settings

## Slide 10
Step 6: Click “File Properties” & check “Save Continuous”. Then click “OK”.

## Slide 11
Step 7: Click “Start Recorder”, wait 5 seconds, click “End Recorder” & then from “File Properties” uncheck “Save Continuous”.

## Slide 12
Step 8: Click “View Files” to view the data file.

## Slide 13
Step 9: Double click on the file to view the data.

## Slide 14
Step 10: Find the instantaneous value in the middle of the IRIG-B signal. In this case the value is 100.

## Slide 15
Step 11: Enter “100” in “Trigger Value” field and make sure the “Trig Type” field is set to “Inst”.

## Slide 16
Step 12: Save the active configuration to disk.

## Slide 17
Step 13: Click “Start Recorder”.

## Slide 18
Step 14: Verify that the Wavewin Sniffer 24 is synchronized.

## Slide 19
Step 15: Click “End Recorder”.

## Slide 20
End of Operations Guide