## Slide 1
The Effect of Fault Impedance Angle on Fault Location
Elevate Energy: Robert Orndorff, Kyle Thomas, Ana Ospina
Softstuf: Amir Makki, Maria Rothweiler

## Slide 2
How can we tell if a Calculated Fault Location is Good or Bad? A good answer is to check the Angle Difference between Line Impedance and Measured Impedance
The following is a tutorial with 7 real life events including Single Phase, Phase to Phase, and 3 Phase examples

## Slide 3
The Main Concept:
Good Location: High Confidence
Bad Location: Medium to Low Confidence But we can Improve

## Slide 4
Summary
If the angle difference is close to zero and the measured fault magnitude is in range with the line impedance magnitude, then it’s a Good Location
 | Z Mag ~ 0 | Z Mag <= Line Z Mag | Z mag > Line Z mag
Angle difference < 10 | High | High | Low
10 < Angle Difference < 40 | High | Medium | Low
Angle Difference > 40 | High | Low | Very Low

## Slide 5
Part I: Single Phase Examples
For AN type Event
Fault Impedance (ZF) =
where K0 =
Fault Location =

## Slide 6
Example-1: Single Phase – Good Angle Difference 500kV - Phase A to Ground - 8kAmps RMS
Angle difference is small and ZF magnitude is reasonable, so the Confidence is High
Va
Vb
Vc
Ia
Ib
Ic
In
Line Z = 10.233 @ 87.76 Ω | Actual = 8.23 miles | LL = 8.77 miles
Fault Z =9.537 @ 89.56 Ω | Calculated = 8.18 miles | Angle Difference = 1.8°

## Slide 7
Example-2: Single Phase - Lightning Strike 115kV - Phase B to Ground - 30kAmps RMS
Angle difference is large but ZF magnitude is almost zero, so the Confidence is High
Line Z1 = 9.615 @ 82.94 Ω | Actual = 0.0 miles | LL = 13.2 miles
Fault Z =0.183 @ 42.26 Ω | Calculated = 0.1 miles | Angle Difference = 40.68°

## Slide 8
Example-3A: Single Phase – Reverse Polarity 230kV - Phase C to Ground - 5kAmps RMS
Angle difference is large and ZF magnitude is not reasonable, so the Confidence is Low
Line Z1 = 6.268 @ 85.401 Ω | Actual = 8.9 miles | LL = 8.37 miles
Fault Z =16.584 @ 48.13 Ω | Calculated = 16.5 miles | Angle Difference = 37.27°

## Slide 9
Example-3B: Single Phase – Reverse Polarity Corrected 230kV - Phase C to Ground - 5kAmps RMS
Angle difference is small and ZF magnitude is reasonable, so the Confidence is High
Line Z1 = 6.268 @ 85.401 Ω | Actual = 8.9 miles | LL = 8.37 miles
Fault Z =6.674 @ 80.96 Ω | Calculated = 8.827 miles | Angle Difference = 4.44°

## Slide 10
Example-4: Single Phase – High Resistance Fault 13.8kV - Phase C to Ground - 3kAmps RMS
Angle difference is large and ZF magnitude is reasonable, so the Confidence is Low
Line Z1 = 2.14 @ 68.86 Ω | Actual = 2.8 miles | LL = 4.84 miles
Fault Z =1.362 @ 25.71 Ω | Calculated = 1.432 miles | Angle Difference = 43.15°

## Slide 11
Part II: Phase to Phase Examples
For an AB type Event
ZF =

## Slide 12
Example-5: Phase to Phase – Small Differences in Z1 and LL 115kV - Phase A to B – 6.1kAmps RMS
Angle difference is not too large and ZF magnitude is reasonable, so the Confidence is High
Line Z1 = 26.806 @ 81.602 Ω | Actual = 14.66 miles | LL = 33.85 miles
Fault Z = 11.93 @ 70.08 Ω | Calculated = 14.815 miles | Angle Difference = 11.522°

## Slide 13
Example-6: Phase to Phase – High Resistance Fault 115kV - Phase A to C – 6.2kAmps RMS
Angle difference is large, but ZF magnitude is low, so the Confidence is High
Line Z1 = 23.537 @ 73.22 Ω | Actual = 0.4 miles | LL = 25.21 miles
Fault Z =1.076 @ 16.37.71 Ω | Calculated = 0.63 miles | Angle Difference = 56.85°

## Slide 14
Part III: Three Phase Example
For an ABC type Event
ZF =
where V1 and I1 are Positive Sequence quantities

## Slide 15
Example-7: Three Phase – Balanced with DC Offset 115kV - Phase ABC – 8.2kAmps RMS
Angle difference is small and ZF magnitude is reasonable, so the Confidence is High
Line Z1 = 28.551 @ 75.607 Ω | Actual = 7.9 miles | LL = 36.46 miles
Fault Z = 6.2621 @ 80.475 Ω | Calculated = 7.968 miles | Angle Difference = 4.868°

## Slide 16
Part IV: Double Ended – Bonus Example
Fault Location (PU) = (VNS – VFS + ZL IFS) / ZL (INS + IFS)
Where the Bus Voltages and Currents are +, 0, or – Sequence Components
VNS = Near side bus voltages
VFS = Far side bus voltages
INS = Near side line currents
IFS = Far side line currents
VF = Fault voltages
IF = Fault currents
RF = Fault resistances
ZL = Line impedance between

## Slide 17
Bonus Example: Double Ended – Works for all Event Types 345kV – Phase CN – 9.5kAmps RMS
Angles are small and Magnitudes add up to LL, so the Confidence is High
Near Side - 6kAmps RMS
Far Side – 3.5kAmps RMS
Near Side Angle = 3.12° | Calculated NS = 19.02 miles | LL = 44.7 miles
Far Side Angle = 2.3° | Calculated FS = 25.76 miles | Actual = 19.1 miles

## Slide 18
 | Z Mag ~ 0 | Z Mag <= Line Z Mag | Z mag > Line Z mag
Angle difference < 10 | High | High | Low
10 < Angle Difference < 40 | High | Medium | Low
Angle Difference > 40 | High | Low | Very Low
Conclusions
The angle difference between measured impedance and line impedance is not often discussed, however the authors have found:
This angle can provide useful information about the (accuracy, quality, correctness, confidence?) of the location calculation.
By looking at the magnitude of the measured fault impedance we get another factor that can be used to determine the confidence of the estimated fault location.
When the measured magnitude is very low, around 5% or less of the line impedance magnitude, then the angle becomes less important in determining confidence.